## 파트장&TO (야간)
TURBINE LOG SHEET(LOCAL) | [7 empty] | Shift Chief | N.Shift
Operator
2026. . . . | [7 empty] | 19:00~07:00 Night Shift
ITEM |  |  | TAG NO. | RATING | UNIT | N/S
[6 empty] | 20 | 23 | 02 | 05
Lube Oil |  | Lube Oil Tank Level | MAV10CL505 | 0~100 | %
|  | Lube Oil Tank Temp. | MAV10CT505 | 43~78 | ℃
|  | Lube Oil Tank Press. | MAV10CP505 | -0.04~0 | barg
|  | Main Oil Pump Discharge Press. | MAV40CP520 | 1.5~3 | barg
|  | Lube Oil Mist Fan #A Ampare | MAV10AN005 | 12 | A
|  | Lube Oil Mist Fan #B Ampare | MAV10AN010 | 12 | A
|  | Generator #7 Bearing Oil Flow | MDK20 | 100~200 | l/m
Control Oil |  | Control Oil Tank Level | MAX10CL010 | 0~100 | %
|  | Control Oil Tank Temp. | MAX10CT505 | 20~58 | ℃
|  | Control Oil Pump Discharge Press. | MAX43CP510 | 100~210 | barg
|  | Air Cooler Suction Press. | MAX30CP510 |  | barg
|  | Control Oil Purifier Humidity | - | 10~20 | %
AVR Room |  | Exciter Module Temp | - | 35~37 | ℃
LP Heater | #1 | #1 LP Heater Inlet Temp. | LCA40CT001 | 43.2 | ℃
|  | #1 LP Heater Level | LCC10CL001 |  | mm
| #2 | #2 LP Heater Inlet Temp. | LCA10CT001 | 85.2 | ℃
|  | #2 LP Heater Level | LCC20CL001 | 360~440 | mm
| #3 | #3 LP Heater Inlet Temp. | LCC20CT001 | 106 | ℃
|  | #3 LP Heater Level | LCC30CL001 | 360~440 | mm
| LP Header | LP Process Steam Header Temp. | LBG20CT001 | 205~215 | ℃
|  | LP Process Steam Header Press. | LBG20CP001 | 0~9.4 | barg
| HP Header | HP Process Steam Header Temp. |  | 230~280 | ℃
|  | HP Process Steam Header Press. |  | 30~35 | barg
CCW Pump | A | Suction Press. | PGB11CP001 | 3.1~3.4 | barg
|  | Discharge Press. | PGB21CP001 | 7~9 | barg
|  | Strainer DIFF. Press. | PGB11CP002 | < 0.2 | barg
| B | Suction Press. | PGB12CP001 | 3.1~3.4 | barg
|  | Discharge Press. | PGB22CP001 | 7~9 | barg
|  | Strainer DIFF. Press. | PGB12CP002 | < 0.2 | barg
ITEM |  |  | TAG NO. | RATING | UNIT | 20 | 23 | 02 | 05
CCW H/E (HOT) A B |  | H/E (CCW) Inlet Temp. | PGB31CT001 | 34~38 | ℃
|  | H/E(CCW) Inlet Press. | PGB31CP001 | - | barg
|  | H/E(CCW) Outlet Temp. | PGB41CT001 | 30~34 | ℃
|  | H/E(CCW) Outlet Press. | PGB41CP001 | - | barg
CCW H/E (COLD) A B |  | H/E (ACW) Inlet Temp. | PCB31CT001 | 28~32 | ℃
|  | H/E(ACW) Inlet Press. | PCB31CP001 | - | barg
|  | H/E(ACW) Outlet Temp. | PCB41CT001 | 30~34 | ℃
|  | H/E(ACW) Outlet Press. | PCB41CP001 | - | barg
Condenser Vacuum Pump A B |  | CVP Suction Press. | MAJ11CP004 | 0.034 | barg
|  | Seal Water Flow | MAJ11CF002 | < 7 | ㎡/h
|  | Seal Water DP | MAJ11CP101 | < 200 | mbara
|  | Seal Water Cooler Inlet Temp. | MAJ11CT004 | 47.52 | ℃
|  | Seal Water Cooler Outlet Temp. | MAJ11CT003 | 37.61 | ℃
Condensate System |  | Condenser Level | MAG10CL001 | 0~100 | %
|  | Condenser Temp. | MAG10CT001 | 80~115 | ℃
|  | Condenser Press. | MAG10CP001 | <-0.8 | barg
|  | Flash Tank Level | MAG20CL001 |  | %
|  | MCWP Condenser Inlet Temp A | PAB41CT001 |  | ℃
|  | MCWP Condenser Outlet Temp A | PAB51CT001 |  | ℃
|  | MCWP Condenser Inlet Temp B | PAB42CT001 |  | ℃
|  | MCWP Condenser Outlet Temp B | PAB52CT001 |  | ℃
Demi Water Pump |  | Suction Press. | GHC11CP001 | - | barg
|  | Discharge Press. | GHC21CP001 | - | barg
Vacuum Breaker |  | Seal Water Filling Condition | MAG10AA005 | - | -
C/T Cell |  | Cell 상태 | 상태 표시 | N/A | -
C/T Vacuum |  | Vacuum Press. |  |  | mbara
태양광 |  | 인버터 상태 | 상태 표시 | N/A | -
전기실 | 본관동 1F | 전기실 상태 | 상태 표시 | N/A | -
|  | Temp |  |  | ℃
| C/W Pump Room | 전기실 상태 | 상태 표시 | N/A | -
|  | Temp |  |  | ℃
| Air Comp Room | 전기실 상태 | 상태 표시 | N/A | -
|  | Temp |  |  | ℃
ITEM |  |  | TAG NO. | RATING | UNIT | 20 | 23 | 02 | 05
BFP | A | Suction Press | LAC11CP001 | 2~16 | barg
|  | Discharge Press | LAC11CP003 | 197.7 | barg
|  | Balance Leak-Off Line Press | LAC11CP003 | 18 | barg
|  | Mechanical Seal Temp(NDE/DE) | LAC11CT001/2 | < 175 | ℃
|  | Lube Oil Press (오리피스 후단) | LCA11CP005 | 0.3 < | barg
|  | Working Oil Temp | LCA11CT003 | < 100 | ℃
| B | Suction Press | LAC12CP001 | 2~16 | barg
|  | Discharge Press | LAC12CP003 | 197.7 | barg
|  | Balance Leak-Off Line Press | LAC11CP003 | 18 | barg
|  | Mechanical Seal Temp(NDE/DE) | LAC12CT001/2 | < 175 | ℃
|  | Lube Oil Press (오리피스 후단) | LCA12CP005 | 0.3 < | barg
|  | Working Oil Temp | LCA12CT003 | < 100 | ℃
| C | Suction Press | LAC12CP001 | 2~16 | barg
|  | Discharge Press | LAC12CP003 | 197.7 | barg
|  | Balance Leak-Off Line Press | LAC11CP003 | 18 | barg
|  | Mechanical Seal Temp(NDE/DE) | LAC12CT001/2 | < 175 | ℃
|  | Lube Oil Press (오리피스 후단) | LCA12CP005 | 0.3 < | barg
|  | Working Oil Temp | LCA12CT003 | < 100 | ℃
COP | A | Suction Press. | LCA11CP001 | -0.9 | barg
|  | Discharge Press. | LCA21CP001 | 20~24 | barg
| B | Suction Press. | LCA12CP001 | -0.9 | barg
|  | Discharge Press. | LCA22CP001 | 20~24 | barg
| C | Suction Press. | LCA13CP001 | -0.9 | barg
|  | Discharge Press. | LCA23CP001 | 20~24 | barg
ACWP | A | Suction Press. | PCB11CP001 | 0.3 | barg
|  | Discharge Press. | PCB21CP001 | 3.2 | barg
| B | Suction Press. | PCB12CP001 | 0.3 | barg
|  | Discharge Press. | PCB22CP001 | 3.2 | barg
MCWP | A | Suction Press. | PAB11CP001 | 0.3 | barg
|  | Discharge Press. | PAB21CP001 | 2.9 | barg
| B | Suction Press. | PAB12CP001 | 0.3 | barg
|  | Discharge Press. | PAB22CP001 | 2.9 | barg
주제어동 옥상 |  | 공조기 | 상태 표시 | N/A | -
주제어동 지하 |  | 공조기 | 상태 표시 | N/A | -
|  | Sump Pump | 상태 표시 | N/A | -
위험물 안전점검 |  | 위험물 일반취급소(TBN동 L.O Tank: 48,000ℓ) |  | 소량 위험물 취급소(비상발전기실 L.O Tank: 990ℓ) |  |  |  | 소량 위험물 저장소(소화전 엔진펌프룸 L.O Tank: 200ℓ)
|  | 점검 내용 | 상태 | 점검 내용 |  |  | 상태 | 상태 | 상태
|  | Oil Tank의 Oil이 유출되지 않는가 | 양호 / 불량 | Oil Tank의 Oil이 유출되지 않는가 |  |  | 양호 / 불량 | Oil Tank의 Oil이 유출되지 않는가 | 양호 / 불량
|  | 환기 및 통풍상태가 양호한가 | 양호 / 불량 | 환기 및 통풍상태가 양호한가 |  |  | 양호 / 불량 | 환기 및 통풍상태가 양호한가 | 양호 / 불량
|  | 소화기 배치, 화재 수신반 양호한가 | 양호 / 불량 | 소화기 배치, 화재 수신반 양호한가 |  |  | 양호 / 불량 | 소화기 배치, 화재 수신반 양호한가 | 양호 / 불량
|  | 주변 발화 요인이 없는가 | 양호 / 불량 | 주변 발화 요인이 없는가 |  |  | 양호 / 불량 | 주변 발화 요인이 없는가 | 양호 / 불량
|  | 주변 청결상태가 양호한가 | 양호 / 불량 | 주변 청결상태가 양호한가 |  |  | 양호 / 불량 | 주변 청결상태가 양호한가 | 양호 / 불량

## BO1&2 Night
BOILER #1&2 LOG SHEET(LOCAL) | [10 empty] | Shift Chief | # 1BLR |  | # 2BLR
Operator
2026. . . . | [11 empty] | 19:00~07:00 Night Shift
ITEM |  |  |  |  | TAG NO. | RATING | UNIT | #1 BLR N/S |  |  |  | #2 BLR N/S
[8 empty] | 20 | 23 | 02 | 05 | 20 | 23 | 02 | 05
Drum |  | Press |  |  | HAD10CP001 | <195.7 | barg
COD & Cyclone 상부 Temp |  | COD L /R |  |  | - | 90 ~ 130 | ℃
|  | Cyclone 상부 L/R |  |  | - | 90 ~ 130 | ℃
Day Silo |  | CO 농도 A / B / Bio |  |  | SGJ00CX202 | 0 | ppm | / / |  | / / |  | / / |  | / /
SDA |  | Atomizer(A,B,C) |  |  | HT2(1,2,3)BN701 | - | - | / / | / / | / / | / / | / / | / / | / / | / /
|  | Lube Oil Level |  |  | - | 양호/불량 | -
|  | Feed Pump Press Discharge Press |  |  | HT10CP00X | 5.5~7 | barg
|  | Make-up Pump Discharge Press |  |  | PCB20CP00X | 9 ~ 10 | barg | / | / | / | / | / | / | / | /
|  | Agitator Current (Feed Tk / Solution Tk) |  |  | - | 3 ~ 3.2 | A | / |  | / |  | / |  | /
SCR |  | Pump Discharge Press A |  |  | HS01CP001 | 6 ~ 8 | barg
|  | Pump Discharge Press B |  |  | HS01CP002 | 6 ~ 8 | barg
|  | Atomizing Air Press |  |  | HS10CP012 | 3 | barg
Coal Feeder |  | A Feeder Flow / Belt Speed |  |  | HHE11GH001 | - | Ton/h M/m | / | / | / | / | / | / | / | /
|  | B Feeder Flow / Belt Speed |  |  | HHE12GH001 | - | Ton/h M/m | / | / | / | / | / | / | / | /
|  | C Feeder Flow / Belt Speed |  |  | HHE21GH001 | - | Ton/h M/m | / | / | / | / | / | / | / | /
|  | D Feeder Flow / Belt Speed |  |  | HHE22GH001 | - | Ton/h M/m | / | / | / | / | / | / | / | /
Wall Screw |  | A Feeder Operation |  |  | HHE11AF011 | 양호/불량 | -
|  | B Feeder Operation |  |  | HHE12AF011 | 양호/불량 | -
|  | C Feeder Operation |  |  | HHE21AF011 | 양호/불량 | -
|  | D Feeder Operation |  |  | HHE22AF011 | 양호/불량 | -
Bio Feeder |  | Reclaimer Oil Level |  |  | - | 양호/불량 | -
|  | Rotary 이음 상태 |  |  | - | 양호/불량 | -
FBHE |  | Right Temp |  |  | - | - | ℃
|  | Left Temp | Spiess Valve CCW Flow |  | - | - | ℃
Spiess Valve |  | Right Temp/CCW Flow | Temp |  | - | - | ℃ Ton/h | / |  | / |  | / |  | /
|  | Left Temp/CCW Flow | Temp |  | - | - | ℃ Ton/h | / |  | / |  | / |  | /
Bed Ash Cooler |  | CCW Out Temp (A/B/C) |  |  | HAD01CT201 | - | ℃ | / / |  | / / |  | / / |  | / /
|  | Bed Ash Chute 온도 |  |  | - | >150 | ℃ | / / |  | / / |  | / / |  | / /
고압가스 저장소 (CO2 Room) |  | 점검내용 | [5 empty] | 점검결과 | 비고 | 점검내용 |  |  |  | 점검결과 | 비고
|  | 1. 화기와의 안전거리 유지 여부 | [7 empty] | 6. 안전장치(압력계, 안전밸브)의 적정 여부
|  | 2. 저장소 시설 경계표지 설치 여부 | [7 empty] | 7. 배관 등 표지판 설치 여부
|  | 3. 저장 탱크실 강제 통풍시설 작동 여부 | [7 empty] | 8. Vaporizer의 온도유지 정상 작동 상태 양호 여부
|  | 4. CO2 설비의 기초 부등침하 및 앵커볼트 파손 유무 | [7 empty] | 9. Vaporizer의 압력계, 온도계 상태 적정 여부
|  | 5. CO2 설비의 가스 누출 여부 | [7 empty] | 10. CO2 설비 경보장치 및 이송설비 적정 여부
ITEM |  |  |  |  | TAG NO. | RATING | UNIT | 20 | 23 | 02 | 05 | 20 | 23 | 02 | 05
FBHE Blower | A | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| B | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| C | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
Seal-pot Blower | A | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| B | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| C | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
SAF |  | Oil Level |  |  | - | 양호/불량 | -
|  | 이음 상태 |  |  | - | 양호/불량 | -
|  | CCW Press/Temp |  |  | PGB49CP042 | 3~4/26~34 | barg/℃ | / | / | / | / | / | / | / | /
PAF |  | Oil Level |  |  | - | 양호/불량 | -
|  | 이음 상태 |  |  | - | 양호/불량 | -
|  | CCW Press/Temp |  |  | PGB49CP052 | 3~4/26~34 | barg/℃ | / | / | / | / | / | / | / | /
IDF |  | BRG Vibration |  |  | - | 양호/불량 | -
|  | CCW Press/Temp |  |  | PGB49CT062 | 3~4/26~34 | barg/℃ | / | / | / | / | / | / | / | /
|  | Lube Oil Temp |  |  | MV10CT002 | 15 ~ 25 | ℃
|  | Lube Oil Inlet Press |  |  | MV10CP002 | > 2.5 | barg
|  | Lube Oil Outlet Press |  |  | MV20CP001 | > 2.5 | barg
|  | Oil Tank level |  |  | - | 양호/불량 | -
Start-Up Burner |  | NG Inlet Press |  |  | EK60CP001 | 1.5 ~ 3 | barg
|  | A Press / B Press |  |  | EK61,62CP001 | 1.5 ~ 3 | barg
|  | C Press / D Press |  |  | EK63,64CP001 | 1.5 ~ 3 | barg
일간 Check List
#1 BLR Dust Collector |  | BM M/U Bin DP |  |  | 103HDB01CP002 |  |  |  |  | Bio-SRF Dosing Conveyor DP |  | 104ECY10CP001
|  | Bed Ash Surge Bin DP |  |  | 103HDC01CP001 |  |  |  |  | SDA Unloading DP |  | 104HT20CP052
|  | Bed Ash Silo DP |  |  | 103HDC01CP002 |  |  |  |  | Lime Storage Silo DP |  | 004HT01CP011
|  | Limestone Silo DP |  |  | 103HDC01CP001 |  |  |  |  | Bed Ash Dust Collector DP |  | 103HDC01CP001
#2 BLR Dust Collector |  | BM M/U Bin DP |  |  | 103HDB01CP002 |  |  |  |  | Bio-SRF Dosing Conveyor DP |  | 104ECY10CP001
|  | Bed Ash Surge Bin DP |  |  | 103HDC01CP001 |  |  |  |  | SDA Unloading DP |  | 104HT20CP052
|  | Bed Ash Silo DP |  |  | 103HDC01CP002 |  |  |  |  | Lime Storage Silo DP |  | 004HT01CP011
|  | Limestone Silo DP |  |  | 103HDC01CP001 |  |  |  |  | Bed Ash Dust Collector DP |  | 103HDC01CP001
ITEM |  |  |  |  | TAG NO. | RATING | UNIT | 20 |  | 23 |  | 02 |  | 05
Plant Air Compressor |  | S.A Recive Tank Press |  |  | QEA50CP201 | 7.1 ~ 9.3 | barg
|  | I.A Recive Tank Press |  |  | QEA40CP201 | 7.1 ~ 9.3 | barg
|  | Pre-Filter DP |  |  | QEA61CP201 | 0 ~ 0.4 | barg
|  | After-Filter DP |  |  | QEA81CP201 | 0 ~ 0.4 | barg
|  | Dryer Dew Point |  |  | QEA70GH001 | < -40 | ℃
|  | Compressor A Oil Temp |  |  | QEA10CT014 | 41~50 | ℃
|  | Compressor B Oil Temp |  |  | QEA11CT014 | 41~50 | ℃
|  | Compressor C Oil Temp |  |  | QEA12CT014 | 41~50 | ℃
Turbo Air Compressor |  | Recive Tank A Pressure |  |  | ETG04CP001 | 6 ~ 9 | barg
|  | Recive Tank B Pressure |  |  | ETG04CP002 | 6 ~ 9 | barg
|  | Oil Return Pressure |  |  | - | -2 ~ -1.5 | kpa
|  | Motor Grease State |  |  | - | 양호/불량 | -
|  | Suction Filter DP |  |  | - | > 600 | mmAq
|  | Cooler Bypass Line Drain 배출 0200 |  |  | - | 양호/불량 | -
Fly Ash Aeration Blower | #1 | Belt State ( #A / #B ) |  |  | - | 양호/불량 | - | / |  | / |  | / |  | /
|  | Oil Level ( #A / #B ) |  |  | - | 양호/불량 | - | / |  | / |  | / |  | /
| #2 | Belt State ( #A / #B ) |  |  | - | 양호/불량 | - | / |  | / |  | / |  | /
|  | Oil Level ( #A / #B ) |  |  | - | 양호/불량 | - | / |  | / |  | / |  | /
#1 유기성 고형연료 Day Silo |  | Blower Current ( A / B ) |  |  |  |  | A | / |  | / |  | / |  | /
|  | Rotary Current ( A / B ) |  |  |  |  | A | / |  | / |  | / |  | /
|  | Rotary Frequency ( A / B ) |  |  |  |  | Hz | / |  | / |  | / |  | /
|  | Blower Outlet Press ( A / B ) |  |  |  |  | barg | / |  | / |  | / |  | /
|  | Ejector Outlet Press ( A / B ) |  |  |  |  | barg | / |  | / |  | / |  | /
|  | XV Outlet Temp ( A / B ) |  |  |  |  | ℃ | / |  | / |  | / |  | /
유기성 고형연료Storage Silo #A |  | Vent Fan Current |  |  |  | 3~4 | A
|  | Vent Fan 이음 상태 |  |  |  | 양호/불량 | -
|  | Sight Glass |  |  |  | 양호/불량 | -
유기성 고형연료Storage Silo #B |  | Vent Fan Current |  |  |  | 3~4 | A
|  | Vent Fan 이음 상태 |  |  |  | 양호/불량 | -
|  | Sight Glass |  |  |  | 양호/불량 | -
#2 유기성 고형연료 Day Silo |  | Blower Current ( A / B ) |  |  |  |  | A | / |  | / |  | / |  | /
|  | Vent Filter Fan Current |  |  |  |  | A
|  | Rotary Current |  | ( A / B ) |  |  | A | / |  | / |  | / |  | /
|  | Rotary Frequency |  | ( A / B ) |  |  | Hz | / |  | / |  | / |  | /
|  | Blower Outlet Press ( A / B ) |  |  |  |  | barg | / |  | / |  | / |  | /
|  | Ejector Outlet Press ( A / B ) |  |  |  |  | barg | / |  | / |  | / |  | /
|  | XV Outlet Temp |  | ( A / B ) |  |  | ℃ | / |  | / |  | / |  | /
유기성 고형연료Storage Silo |  | Air Receiver Tank Pressure |  |  |  | 7~8 | barg
|  | Air Lock Feeder 누설 여부 ( A / B ) |  |  |  | N | - | / |  | / |  | / |  | /
|  | Booster Air Pressure ( A / B ) |  |  |  | 7~8 | barg | / |  | / |  | / |  | /

## TO (주간)
TURBINE LOG SHEET(LOCAL) | [7 empty] | Shift Chief | D.Shift
Operator
2026. . . . | [7 empty] | 07:00~19:00 Day Shift
ITEM |  |  | TAG NO. | RATING | UNIT | D/S
[6 empty] | 08 | 11 | 14 | 17
Lube Oil |  | Lube Oil Tank Level | MAV10CL505 | 0~100 | %
|  | Lube Oil Tank Temp. | MAV10CT505 | 43~78 | ℃
|  | Lube Oil Tank Press. | MAV10CP505 | -0.04~0 | barg
|  | Main Oil Pump Discharge Press. | MAV40CP520 | 1.5~3 | barg
|  | Lube Oil Mist Fan #A Ampare | MAV10AN005 | 12 | A
|  | Lube Oil Mist Fan #B Ampare | MAV10AN010 | 12 | A
|  | Generator #7 Bearing Oil Flow | MDK20 | 100~200 | l/m
Control Oil |  | Control Oil Tank Level | MAX10CL010 | 0~100 | %
|  | Control Oil Tank Temp. | MAX10CT505 | 20~58 | ℃
|  | Control Oil Pump Discharge Press. | MAX43CP510 | 100~210 | barg
|  | Air Cooler Suction Press. | MAX30CP510 |  | barg
|  | Control Oil Purifier Humidity | - | 10~20 | %
AVR Room |  | Exciter Module Temp | - | 35~37 | ℃
LP Heater | #1 | #1 LP Heater Inlet Temp. | LCA40CT001 | 43.2 | ℃
|  | #1 LP Heater Level | LCC10CL001 |  | mm
| #2 | #2 LP Heater Inlet Temp. | LCA10CT001 | 85.2 | ℃
|  | #2 LP Heater Level | LCC20CL001 | 360~440 | mm
| #3 | #3 LP Heater Inlet Temp. | LCC20CT001 | 106 | ℃
|  | #3 LP Heater Level | LCC30CL001 | 360~440 | mm
| LP Header | LP Process Steam Header Temp. | LBG20CT001 | 205~215 | ℃
|  | LP Process Steam Header Press. | LBG20CP001 | 0~9.4 | barg
| HP Header | HP Process Steam Header Temp. |  | 230~280 | ℃
|  | HP Process Steam Header Press. |  | 30~35 | barg
CCW Pump | A | Suction Press. | PGB11CP001 | 3.1~3.4 | barg
|  | Discharge Press. | PGB21CP001 | 7~9 | barg
|  | Strainer DIFF. Press. | PGB11CP002 | < 0.2 | barg
| B | Suction Press. | PGB12CP001 | 3.1~3.4 | barg
|  | Discharge Press. | PGB22CP001 | 7~9 | barg
|  | Strainer DIFF. Press. | PGB12CP002 | < 0.2 | barg
ITEM |  |  | TAG NO. | RATING | UNIT | 08 | 11 | 14 | 17
CCW H/E (HOT) A B |  | H/E (CCW) Inlet Temp. | PGB31CT001 | 34~38 | ℃
|  | H/E(CCW) Inlet Press. | PGB31CP001 | - | barg
|  | H/E(CCW) Outlet Temp. | PGB41CT001 | 30~34 | ℃
|  | H/E(CCW) Outlet Press. | PGB41CP001 | - | barg
CCW H/E (COLD) A B |  | H/E (ACW) Inlet Temp. | PCB31CT001 | 28~32 | ℃
|  | H/E(ACW) Inlet Press. | PCB31CP001 | - | barg
|  | H/E(ACW) Outlet Temp. | PCB41CT001 | 30~34 | ℃
|  | H/E(ACW) Outlet Press. | PCB41CP001 | - | barg
Condenser Vacuum Pump A B |  | CVP Suction Press. | MAJ11CP004 | 0.034 | barg
|  | Seal Water Flow | MAJ11CF002 | < 7 | ㎡/h
|  | Seal Water DP | MAJ11CP101 | < 200 | mbara
|  | Seal Water Cooler Inlet Temp. | MAJ11CT004 | 47.52 | ℃
|  | Seal Water Cooler Outlet Temp. | MAJ11CT003 | 37.61 | ℃
Condensate System |  | Condenser Level | MAG10CL001 | 0~100 | %
|  | Condenser Temp. | MAG10CT001 | 80~115 | ℃
|  | Condenser Press. | MAG10CP001 | <-0.8 | barg
|  | Flash Tank Level | MAG20CL001 |  | %
|  | MCWP Condenser Inlet Temp A | PAB41CT001 |  | ℃
|  | MCWP Condenser Outlet Temp A | PAB51CT001 |  | ℃
|  | MCWP Condenser Inlet Temp B | PAB42CT001 |  | ℃
|  | MCWP Condenser Outlet Temp B | PAB52CT001 |  | ℃
Demi Water Pump |  | Suction Press. | GHC11CP001 | - | barg
|  | Discharge Press. | GHC21CP001 | - | barg
Vacuum Breaker |  | Seal Water Filling Condition | MAG10AA005 | - | -
C/T Cell |  | Cell 상태 | 상태 표시 | N/A | -
C/T Vacuum |  | Vacuum Press. |  |  | mbara
태양광 |  | 인버터 상태 | 상태 표시 | N/A | -
전기실 | 본관동 1F | 전기실 상태 | 상태 표시 | N/A | -
|  | Temp |  |  | ℃
| C/W Pump Room | 전기실 상태 | 상태 표시 | N/A | -
|  | Temp |  |  | ℃
| Air Comp Room | 전기실 상태 | 상태 표시 | N/A | -
|  | Temp |  |  | ℃
ITEM |  |  | TAG NO. | RATING | UNIT | 08 | 11 | 14 | 17
BFP | A | Suction Press | LAC11CP001 | 2~16 | barg
|  | Discharge Press | LAC11CP003 | 197.7 | barg
|  | Balance Leak-Off Line Press | LAC11CP003 | 18 | barg
|  | Mechanical Seal Temp(NDE/DE) | LAC11CT001/2 | < 175 | ℃
|  | Lube Oil Press (오리피스 후단) | LCA11CP005 | 0.3 < | barg
|  | Working Oil Temp | LCA11CT003 | < 100 | ℃
| B | Suction Press | LAC12CP001 | 2~16 | barg
|  | Discharge Press | LAC12CP003 | 197.7 | barg
|  | Balance Leak-Off Line Press | LAC11CP003 | 18 | barg
|  | Mechanical Seal Temp(NDE/DE) | LAC12CT001/2 | < 175 | ℃
|  | Lube Oil Press (오리피스 후단) | LCA12CP005 | 0.3 < | barg
|  | Working Oil Temp | LCA12CT003 | < 100 | ℃
| C | Suction Press | LAC12CP001 | 2~16 | barg
|  | Discharge Press | LAC12CP003 | 197.7 | barg
|  | Balance Leak-Off Line Press | LAC11CP003 | 18 | barg
|  | Mechanical Seal Temp(NDE/DE) | LAC12CT001/2 | < 175 | ℃
|  | Lube Oil Press (오리피스 후단) | LCA12CP005 | 0.3 < | barg
|  | Working Oil Temp | LCA12CT003 | < 100 | ℃
COP | A | Suction Press. | LCA11CP001 | -0.9 | barg
|  | Discharge Press. | LCA21CP001 | 20~24 | barg
| B | Suction Press. | LCA12CP001 | -0.9 | barg
|  | Discharge Press. | LCA22CP001 | 20~24 | barg
| C | Suction Press. | LCA13CP001 | -0.9 | barg
|  | Discharge Press. | LCA23CP001 | 20~24 | barg
ACWP | A | Suction Press. | PCB11CP001 | 0.3 | barg
|  | Discharge Press. | PCB21CP001 | 3.2 | barg
| B | Suction Press. | PCB12CP001 | 0.3 | barg
|  | Discharge Press. | PCB22CP001 | 3.2 | barg
MCWP | A | Suction Press. | PAB11CP001 | 0.3 | barg
|  | Discharge Press. | PAB21CP001 | 2.9 | barg
| B | Suction Press. | PAB12CP001 | 0.3 | barg
|  | Discharge Press. | PAB22CP001 | 2.9 | barg
주제어동 옥상 |  | 공조기 | 상태 표시 | N/A | -
주제어동 지하 |  | 공조기 | 상태 표시 | N/A | -
|  | Sump Pump | 상태 표시 | N/A | -

## BO1
BOILER #1 LOG SHEET(LOCAL) | [8 empty] | Shift Chief | D.Shift
Operator
2026. . . . | [8 empty] | 07:00~19:00 Day Shift
ITEM |  |  |  | TAG NO. | RATING | UNIT | D/S
[7 empty] | 08 | 11 | 14 | 17
Drum |  | Press |  | HAD10CP001 | <195.7 | barg
COD & Cyclone 상부 Temp |  | COD L /R |  | - | 90 ~ 130 | ℃
|  | Cyclone 상부 L/R |  | - | 90 ~ 130 | ℃
Day Silo |  | CO 농도 A / B / Bio |  | SGJ00CX202 | 0 | ppm | / / |  | / /
SDA |  | Atomizer(A,B,C) |  | HT2(1,2,3)BN701 | - | - | / / | / / | / / | / /
|  | Lube Oil Level |  | - | 양호/불량 | -
|  | Feed Pump Press Discharge Press |  | HT10CP00X | 5.5~7 | barg
|  | Make-up Pump Discharge Press |  | PCB20CP00X | 9 ~ 10 | barg | / | / | / | /
|  | Agitator Current (Feed Tk / Solution Tk) |  | - | 3 ~ 3.2 | A | / |  | /
SCR |  | Pump Discharge Press A |  | HS01CP001 | 6 ~ 8 | barg
|  | Pump Discharge Press B |  | HS01CP002 | 6 ~ 8 | barg
|  | Atomizing Air Press |  | HS10CP012 | 3 | barg
Coal Feeder |  | A Feeder Flow / Belt Speed |  | HHE11GH001 | - | Ton/h M/m | / | / | / | /
|  | B Feeder Flow / Belt Speed |  | HHE12GH001 | - | Ton/h M/m | / | / | / | /
|  | C Feeder Flow / Belt Speed |  | HHE21GH001 | - | Ton/h M/m | / | / | / | /
|  | D Feeder Flow / Belt Speed |  | HHE22GH001 | - | Ton/h M/m | / | / | / | /
Wall Screw |  | A Feeder Operation |  | HHE11AF011 | 양호/불량 | -
|  | B Feeder Operation |  | HHE12AF011 | 양호/불량 | -
|  | C Feeder Operation |  | HHE21AF011 | 양호/불량 | -
|  | D Feeder Operation |  | HHE22AF011 | 양호/불량 | -
Bio Feeder |  | Reclaimer Oil Level |  | - | 양호/불량 | -
|  | Rotary 이음 상태 |  | - | 양호/불량 | -
FBHE |  | Right Temp |  | - | - | ℃
|  | Left Temp | Spiess Valve CCW Flow | - | - | ℃
Spiess Valve |  | Right Temp/CCW Flow | Temp | - | - | ℃ Ton/h | / |  | /
|  | Left Temp/CCW Flow | Temp | - | - | ℃ Ton/h | / |  | /
Bed Ash Cooler |  | CCW Out Temp (A/B/C) |  | HAD01CT201 | - | ℃ | / / |  | / /
|  | Bed Ash Chute 온도 |  | - | >150 | ℃ | / / |  | / /
ITEM |  |  |  | TAG NO. | RATING | UNIT | 08 | 11 | 14 | 17
FBHE Blower | A | Belt State |  | - | 양호/불량 | -
|  | Oil Level |  | - | 양호/불량 | -
| B | Belt State |  | - | 양호/불량 | -
|  | Oil Level |  | - | 양호/불량 | -
| C | Belt State |  | - | 양호/불량 | -
|  | Oil Level |  | - | 양호/불량 | -
Seal-pot Blower | A | Belt State |  | - | 양호/불량 | -
|  | Oil Level |  | - | 양호/불량 | -
| B | Belt State |  | - | 양호/불량 | -
|  | Oil Level |  | - | 양호/불량 | -
| C | Belt State |  | - | 양호/불량 | -
|  | Oil Level |  | - | 양호/불량 | -
SAF |  | Oil Level |  | - | 양호/불량 | -
|  | 이음 상태 |  | - | 양호/불량 | -
|  | CCW Press/Temp |  | PGB49CP042 | 3~4/26~34 | barg/℃ | / | / | / | /
PAF |  | Oil Level |  | - | 양호/불량 | -
|  | 이음 상태 |  | - | 양호/불량 | -
|  | CCW Press/Temp |  | PGB49CP052 | 3~4/26~34 | barg/℃ | / | / | / | /
IDF |  | BRG Vibration |  | - | 양호/불량 | -
|  | CCW Press/Temp |  | PGB49CT062 | 3~4/26~34 | barg/℃ | / | / | / | /
|  | Lube Oil Temp |  | MV10CT002 | 15 ~ 25 | ℃
|  | Lube Oil Inlet Press |  | MV10CP002 | > 2.5 | barg
|  | Lube Oil Outlet Press |  | MV20CP001 | > 2.5 | barg
|  | Oil Tank level |  | - | 양호/불량 | -
Plant Air Compressor |  | S.A Recive Tank Press |  | QEA50CP201 | 7.1 ~ 9.3 | barg
|  | I.A Recive Tank Press |  | QEA40CP201 | 7.1 ~ 9.3 | barg
|  | Pre-Filter DP |  | QEA61CP201 | 0 ~ 0.4 | barg
|  | After-Filter DP |  | QEA81CP201 | 0 ~ 0.4 | barg
|  | Dryer Dew Point |  | QEA70GH001 | < -40 | ℃
|  | Compressor A Oil Temp |  | QEA10CT014 | 41~50 | ℃
|  | Compressor B Oil Temp |  | QEA11CT014 | 41~50 | ℃
|  | Compressor C Oil Temp |  | QEA12CT014 | 41~50 | ℃
유기성 고형연료 Day Silo |  | Blower Current ( A / B ) |  |  |  | A | / | / | / | /
|  | Rotary Current ( A / B ) |  |  |  | A | / | / | / | /
|  | Rotary Frequency ( A / B ) |  |  |  | Hz | / | / | / | /
|  | Blower Outlet Press ( A / B ) |  |  |  | barg | / | / | / | /
|  | Ejector Outlet Press ( A / B ) |  |  |  | barg | / | / | / | /
|  | Blower Oil 및 Belt 상태 ( A / B ) |  |  |  | 양호/불량 | / | / | / | /
ITEM |  |  |  | TAG NO. | RATING | UNIT | 08 | 11 | 14 | 17
유기성 고형연료Storage Silo #A |  | Vent Fan Current |  |  | 3~4 | A
|  | Vent Fan 이음 상태 |  |  | 양호/불량 | -
|  | Sight Glass |  |  | 양호/불량 | -
|  | Mode |  |  | Auto | -
유기성 고형연료Storage Silo #B |  | Vent Fan Current |  |  | 3~4 | A
|  | Vent Fan 이음 상태 |  |  | 양호/불량 | -
|  | Sight Glass |  |  | 양호/불량 | -
|  | Mode |  |  | Auto | -
Start-Up Burner |  | NG Inlet Press |  | EK60CP001 | 1.5 ~ 3 | barg
|  | A Press / B Press |  | EK61,62CP001 | 1.5 ~ 3 | barg
|  | C Press / D Press |  | EK63,64CP001 | 1.5 ~ 3 | barg
Coal Feeder Panel Cooling Fan |  | Fan Motor Current (A/B) |  | - | < 5 | A
|  |  |  | - | < 5 | A
|  | humidity (Inverter Panel #D) |  | - | - | %

## BO2
BOILER #2 LOG SHEET(LOCAL) | [9 empty] | Shift Chief | D.Shift
Operator
2026. . . . | [9 empty] | 07:00~19:00 Day Shift
ITEM |  |  |  |  | TAG NO. | RATING | UNIT | D/S
[8 empty] | 08 | 11 | 14 | 17
Drum |  | Press |  |  | HAD10CP001 | <195.7 | barg
COD & Cyclone 상부 Temp |  | COD L /R |  |  | - | 90 ~ 130 | ℃
|  | Cyclone 상부 L/R |  |  | - | 90 ~ 130 | ℃
Day Silo |  | CO 농도 A / B / Bio |  |  | SGJ00CX202 | 0 | ppm | / / |  | / /
SDA |  | Atomizer(A,B,C) |  |  | HT2(1,2,3)BN701 | - | - | / / | / / | / / | / /
|  | Lube Oil Level |  |  | - | 양호/불량 | -
|  | Feed Pump Press Discharge Press |  |  | HT10CP00X | 5.5~7 | barg
|  | Make-up Pump Discharge Press |  |  | PCB20CP00X | 9 ~ 10 | barg | / | / | / | /
|  | Agitator Current (Feed Tk / Solution Tk) |  |  | - | 3 ~ 3.2 | A | / |  | /
SCR |  | Pump Discharge Press A |  |  | HS01CP001 | 6 ~ 8 | barg
|  | Pump Discharge Press B |  |  | HS01CP002 | 6 ~ 8 | barg
|  | Atomizing Air Press |  |  | HS10CP012 | 3 | barg
Coal Feeder |  | A Feeder Flow / Belt Speed |  |  | HHE11GH001 | - | Ton/h M/m
|  | B Feeder Flow / Belt Speed |  |  | HHE12GH001 | - | Ton/h M/m
|  | C Feeder Flow / Belt Speed |  |  | HHE21GH001 | - | Ton/h M/m
|  | D Feeder Flow / Belt Speed |  |  | HHE22GH001 | - | Ton/h M/m
Wall Screw |  | A Feeder Operation |  |  | HHE11AF011 | 양호/불량 | -
|  | B Feeder Operation |  |  | HHE12AF011 | 양호/불량 | -
|  | C Feeder Operation |  |  | HHE21AF011 | 양호/불량 | -
|  | D Feeder Operation |  |  | HHE22AF011 | 양호/불량 | -
Bio Feeder |  | Reclaimer Oil Level |  |  | - | 양호/불량 | -
|  | Rotary 이음 상태 |  |  | - | 양호/불량 | -
FBHE |  | Right Temp |  |  | - | - | ℃
|  | Left Temp | Spiess Valve CCW Flow |  | - | - | ℃
Spiess Valve |  | Right Temp/CCW Flow | Temp |  | - | - | ℃ | / |  | /
|  | Left Temp/CCW Flow | Temp |  | - | - | Ton/h | / |  | /
ITEM |  |  |  |  | TAG NO. | RATING | UNIT | 08 | 11 | 14 | 17
Bed Ash Cooler |  | CCW Out Temp (A/B/C) |  |  | HAD01CT201 | - | ℃ | / / |  | / /
|  | Bed Ash Chute 온도 |  |  | - | >150 | ℃ | / / |  | / /
FBHE Blower | A | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| B | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| C | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
Seal-pot Blower | A | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| B | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| C | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
SAF |  | Oil Level |  |  | - | 양호/불량 | -
|  | 이음 상태 |  |  | - | 양호/불량 | -
|  | CCW Press/Temp |  |  | PGB49CP042 | 3~4/26~34 | barg/℃ | / | / | / | /
PAF |  | Oil Level |  |  | - | 양호/불량 | -
|  | 이음 상태 |  |  | - | 양호/불량 | -
|  | CCW Press/Temp |  |  | PGB49CP052 | 3~4/26~34 | barg/℃ | / | / | / | /
IDF |  | BRG Vibration |  |  | - | 양호/불량 | -
|  | CCW Press/Temp |  |  | PGB49CT062 | 3~4/26~34 | barg/℃ | / | / | / | /
|  | Lube Oil Temp |  |  | MV10CT002 | 15 ~ 25 | ℃
|  | Lube Oil Inlet Press |  |  | MV10CP002 | > 2.5 | barg
|  | Lube Oil Outlet Press |  |  | MV20CP001 | > 2.5 | barg
|  | Oil Tank level |  |  | - | 양호/불량 | N/A
Turbo Air Compressor |  | Recive Tank A Pressure |  |  | ETG04CP001 | 6 ~ 9 | barg
|  | Recive Tank B Pressure |  |  | ETG04CP002 | 6 ~ 9 | barg
|  | Oil Return Pressure |  |  | - | -2 ~ -1.5 | kpa
|  | Motor Grease State |  |  | - | 양호/불량 | -
|  | Suction Filter DP |  |  | - | > 600 | mmAq
|  | Cooler Bypass Line Drain 배출 0200 |  |  | - | 양호/불량 | -
Fly Ash Aeration Blower | A | Belt State |  |  | - | 양호/불량 | -
|  | Oil Level |  |  | - | 양호/불량 | -
| B | Belt State |  |  | - | 양호/불량 | - | `
|  | Oil Level |  |  | - | 양호/불량 | -
ITEM |  |  |  |  | TAG NO. | RATING | UNIT | 08 | 11 | 14 | 17
유기성 고형연료 |  | Blower Current ( A / B ) |  |  |  | 44~50 | A | / | / | / | /
|  | Vent Filter Fan Current |  |  |  | 1.2~1.8 | A
|  | Rotary Current |  | ( A / B ) |  | 0.6~1.6 | A | / | / | / | /
|  | Rotary Frequency |  | ( A / B ) |  |  | Hz | / | / | / | /
|  | Blower Outlet Press ( A / B ) |  |  |  |  | barg | / | / | / | /
|  | Ejector Outlet Press ( A / B ) |  |  |  |  | barg | / | / | / | /
|  | Blower Oil 및 Belt 상태 ( A / B ) |  |  |  | 양호/불량 |  | / | / | / | /
유기성 고형연료Storage Silo |  | Air Receiver Tank Pressure |  |  |  | 7~8 | barg
|  | Booster Air Pressure ( A / B ) |  |  |  | 7~8 | barg
|  | Air Lock Feeder 누설 여부 ( A / B ) |  |  |  | N | -
Start-Up Burner |  | NG Inlet Press |  |  | EK60CP001 | 1.5 ~ 3 | barg
|  | A Press / B Press |  |  | EK61,62CP001 | 1.5 ~ 3 | barg | / | / | / | /
|  | C Press / D Press |  |  | EK63,64CP001 | 1.5 ~ 3 | barg | / | / | / | /