## 고압보조보일러 제어실
고압 보조보일러 제어실 Log Sheet | [13 empty] | Shift Chief | D.Shift |  | N.Shift
Operator
2026 년 월 일 | [6 empty] | 07:00~19:00 Day Shift | [5 empty] | 19:00~07:00 Night Shift
Check Item |  |  | Tag No | Unit | Setting |  | D/S | [5 empty] | N/S
[7 empty] | 08 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 02 | 04 | 06
[5 empty] | Normal | Trip
Main Steam | Flow (Average) |  | CF901 | T/H
| Pressure (Average) |  | CP901 | bar
| Temperature |  | CT201 | ℃
Drum | Pressure (Medium) |  | CP901 | bar | 35
| Level (Medium) |  | CL901 | mm | 0
Boiler Feed Water | Flow (Average) |  | F901 | T/H
| Pressure (Average) |  | P901 | Bar.g | 17.9
| Temperature |  | CT201 | ℃
Blow Down | Flow |  | F201 | kg/h
Economizer | Water Temperature |  | T201 | ℃ | 155
LNG Gas | Pressure (Medium) |  | P901 | Bar.g
| Temperature |  | T201 | ℃
| Flow |  | F201 | Nm3/h
Burner | LNG Pressure (Medium) |  | P911 | Bar.g | 0.7 | HH:1.1
Pilot Burner | Pressure |  | P201 | Bar.g | 0.5
Air Flow | Wind Box Pressure |  | P201 | mmH2O | 435
Boiler | Pressure (Medium) |  | P901 | mmH2O | 130 | HH:400
Flue Gas | SCR | Inlet Pressure | 20CP201 | mmH2O
|  | Outlet Pressure | 30CP201 | mmH2O
|  | Difference Pressure | 30CP202 | mmH2O
| Temperature |  | T201 | ℃ | 356 | 370
| O2 |  | Q001 | % | 2
| ECO | Out Pressure | P201 | mmH2O | 20
|  | Out Temperature | T201 | ℃ | 178
FD Fan | 개도 |  | CG210 | %
| Load |  | AN201 | A | 32.7
| Outlet Pressure |  | P201 | mmH2O | 435
| Outlet Temperature |  | T201 | ℃ | 25
| Flow (Medium) |  | F901 | KNm3/h | 94 | LL:6.5
| Winding Temperature |  | T201~3 | ℃ | 100
| Bearing Temperature |  | T204~7 | ℃ | 60
| Vibration |  | S001~4 | mm/s | 2
Check Item |  |  | Tag No | Unit | Setting |  | D/S 08: D/S; N/S 20: N/S
[7 empty] | 08 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 02 | 04 | 06
[5 empty] | Normal | Trip
Sampling | pH | Aux. BLR Steam Line | Q001 | pH | 10
| CC |  | Q002 | ㎲/Cm | 0.3
| pH | Aux. BLR Steam Drum | Q001 | pH | 10.5
| CC |  | Q002 | ㎲/Cm | 30
| pH | BFW Pump Suction | Q001 | pH | 10.5
| DO |  | Q002 | PPb | 3
| CC |  | Q003 | ㎲/Cm | 30
| pH | Deaerator Feed Water | Q001 | pH | 10.5
| DO |  | Q002 | PPb | 3
| CC |  | Q003 | ㎲/Cm | 30
Air Compressor | Instrument Pre Filter Difference Pressure |  | P202 | mmH2O | 40
| Instrument After Filter Difference Pressure |  | P211 | mmH2O | 40
| Instrument Outlet Pressure |  | P901 | Bar.g | 7 | 5
| Service Outlet Pressure |  | P201 | Bar.g | 7 | 5
Blowdown Tank | Level |  | L201 | % | 0
| Temperature |  | T201 | ℃ | 40
Closed Cooling Water | #1 | Difference Pressure | C11CP201 | mmH2O | 2000
| #2 |  | C12CP201 | mmH2O | 2000
| Outlet Pressure |  | C30CP201 | Bar.g | 4
| Outlet Temperature |  | C50CT201 | ℃ | 40
Deaerator | Water Temperature |  | C50CT201 | ℃
| Pressure |  | P901 | Bar.g | 0.2
| Pegging Steam Flow |  | 31CF201 | T/H
Feed Water Storage Tank | Level |  | L901 | mm | 0
| Temperature |  | T201 | ℃ | 105
Feed Water Pump | #1 | Difference Pressure | 11CP201 | mmH2O |  | 4000
|  | Shaft Vibration(NDE-Z) | 001CS005 | ㎛ | 80 | HH:400
| #2 | Difference Pressure | 12CP201 | mmH2O |  | 4000
|  | Shaft Vibration(NDE-Z) | 002CS005 | ㎛ | 80 | HH:400
Ammonia Storage Tank | Difference Pressure |  | P201 | mmH2O
| Level |  | L201 | %
SCR | NOx |  | 407Q011 | ppm | 40
| NH3 |  | 407Q012 | ppm | 10
| Ammonia Flow |  | 407S30F201 | L/H | 24
| Service Air Flow |  | 407B40P201 | Bar.g | 3.2
| Inlet Temperature |  | 407N20T201 | ℃ | 200 | LL:195
| Outlet Temperature |  | 407S90T201 | ℃ | 100 | LL:80
Softener | #1 | Outlet Flow | F201 | T/H | 30
| #2 |  | F202 | T/H | 30
| Outlet pH |  | Q001 | ppm | 10
| Raw Water Storage Tank Level |  | CL201 | mm